## Sheet1
Fault Analysis Table
| F1 |  | F2 |  | F3 |  | F5 |  | F6 |  | F9 |  | F10 |  | F11 |  | F12 |  | F13 |  | FB5 |  | FB8 |  | FB14 |  | FB15 |  | FB16 |  | FB17 |  | FB18 |  | FB19 |  | FB20 |  | FB21
Circuit Beaker | Involved | Trip | Involved | Trip | Involved | Trip | Involved | Trip | Involved | Trip | Involved | Trip | Involved | Trip | Involved | Trip | Involved | Trip | Involved | Trip | Involved | Trip | Involved | Trip | Involved | Trip | Involved | Trip | Involved | Trip | Involved | Trip | Involved | Trip | Involved | Trip | Involved | Trip | Involved | Trip
CB1 | x | x
CB2 |  |  | x | x
CB3 |  |  |  | x | x
CB5 | x |  | x | x |  |  | x | x
CB6 | [8 empty] | x | x
CB7 | x |  | x |  | x |  | x |  | x |  | x |  | x |  | x |  | x |  | x |  | x | x | x |  | x |  | x |  | x |  | x |  | x | x | x |  | x |  | x
CB8 | x |  | x |  | x |  | x |  | x |  | x |  | x |  | x |  | x |  | x |  | x | x | x | x | x |  | x |  | x |  | x |  | x |  | x |  | x |  | x
CB9 | [10 empty] | x | x
CB10 | [12 empty] | x | x
CB11 | [14 empty] | x | x
CB12 | [10 empty] | x |  | x |  |  |  | x | x
CB13 | [10 empty] | x |  | x |  | x |  | x |  | x | x
CB14 | x |  | x | x |  |  | x |  | x |  | x |  | x |  | x |  | x |  | x |  | x |  | x |  | x | x | x |  | x |  | x |  | x | x | x |  | x |  | x
CB15 | x |  | x | x |  |  | x |  | x |  | x |  | x |  | x |  | x |  | x |  | x |  | x |  | x |  | x | x | x |  | x |  | x |  | x | x | x |  | x
CB16 | x |  | x | x |  |  | x |  | x |  | x |  | x |  | x |  | x |  | x |  | x |  | x |  | x |  | x |  | x | x | x | x | x |  | x |  | x |  | x
CB17 | x |  | x | x |  |  | x |  | x |  | x |  | x |  | x |  | x |  | x |  | x | x | x |  | x |  | x |  | x |  | x | x | x |  | x |  | x |  | x
CB18 | x |  | x | x |  |  | x |  | x |  | x |  | x |  | x |  | x |  | x |  | x |  | x |  | x |  | x |  | x |  | x |  | x | x | x |  | x |  | x
CB19 | x |  | x | x |  |  | x |  | x |  | x |  | x |  | x |  | x |  | x |  | x |  | x |  | x |  | x |  | x |  | x |  | x |  | x | x | x |  | x
CB20 | x |  | x | x |  |  | x |  | x |  | x |  | x |  | x |  | x |  | x |  | x |  | x |  | x |  | x |  | x |  | x |  | x |  | x | x | x | x | x
CB21 | x |  | x | x |  |  | x |  | x |  | x |  | x |  | x |  | x |  | x |  | x |  | x |  | x |  | x |  | x |  | x |  | x |  | x |  | x | x | x | x
CB settings
Circuit Breaker | L |  |  | S
| Iioc [A] | I1 | t1 | Function | I7 | t7 FWD | t7 BWD | Zone Selectivity status | t2 sel | I2 | t2 | I3 | t3
|  | [xIn] | [s] |  | [xIn] | [s] | [s] |  | [s] | [A] | [s] | [A] | [s]
CB1 | 200 | 250 | 10 | t=k |  |  |  | Disabled | 0.1 | 500 | 0.2 | - | -
CB2 | 200 | 250 | 10 | t=k |  |  |  | Disabled | 0.1 | 500 | 0.2 | - | -
CB3 | 200 | 250 | 10 | t=k |  |  |  | Disabled | 0.1 | 500 | 0.2 | - | -
CB5 | 600 | 750 | 12 | t=k |  |  |  | Disabled | 0.1 | 1500 | 0.3 | - | -
CB6 | 200 | 250 | 10 | t=k |  |  |  | Disabled | 0.1 | 500 | 0.2 | - | -
CB8 | 350 | 800 | 16 | t=k | 1600 | 0.5 | 0.5 | Enable | 0.1 | - | - | - | -
CB9 | 200 | 250 | 10 | t=k |  |  |  | Disabled | 0.1 | 500 | 0.2 | - | -
CB10 | 200 | 250 | 10 | t=k |  |  |  | Disabled | 0.1 | 500 | 0.2 | - | -
CB11 | 450 | 600 | 10 | t=k |  |  |  | Disabled | 0.1 | 1200 | 0.2 | - | -
CB12 | 400 | 500 | 12 | t=k |  |  |  | Disabled | 0.1 | 1000 | 0.3 | - | -
CB13 | 850 | 1200 | 14 | t=k |  |  |  | Disabled | 0.1 | 2400 | 0.4 | - | -
CB14 | 350 | 800 | 16 | t=k | 1600 | 0.5 | 0.5 | Enable | 0.1 | - | - | - | -
CB15 | 350 | 800 | 16 | t=k | 1600 | 0.5 | 0.7 | Enable | 0.1 | - | - | - | -
CB16 | 350 | 800 | 16 | t=k | 1600 | 0.5 | 0.5 | Enable | 0.1 | - | - | - | -
CB17 | 350 | 800 | 16 | t=k | 1600 | 0.5 | 0.5 | Enable | 0.1 | - | - | - | -
CB7 | 100 | 1300 | 16 | t=k | 2600 | 0.5 | 0.5 | Enable | 0.1 | - | - | - | -
CB18 | 250 | 1000 | 16 | t=k | 2000 | 0.5 | 0.5 | Enable | 0.1 | - | - | - | -
CB19 | 350 | 800 | 16 | t=k | 1600 | 0.7 | 0.5 | Enable | 0.1 | - | - | - | -
CB20 | 250 | 800 | 16 | t=k | 1600 | 0.5 | 0.5 | Enable | 0.1 | - | - | - | -
CB21 | 250 | 800 | 16 | t=k | 1600 | 0.5 | 0.5 | Enable | 0.1 | - | - | - | -
Ekip Link Table |  | f = 1 | b = 0
CB | Actor 1 | Actor 2 | Actor 3 | Actor 4 | Actor 5 | Actor 6 | Actor 7
CB1 | bar: Actor 1 to b = 0 Actor 7
CB2 | bar: Actor 1 to b = 0 Actor 7
CB3 | bar: Actor 1 to b = 0 Actor 7
CB5 | bar: Actor 1 to b = 0 Actor 7
CB6 | bar: Actor 1 to b = 0 Actor 7
CB7 | CB5 Dfo->Dbi | CB8 Dbo->Dbi | CB17 Dbo->Dbi | CB6 Dfo->Dfi | CB14 Dbo->Dfi | CB18 Dfo->Dfi | [5 empty] | CB Dfo->Dfi | CB Dfo->Dbi |  | CB Dbo->Dbi | CB Dbo->Dfi
CB8 | Actor 1: CB5 Dfo->Dfi; f = 1 Actor 2: CB7 Dfo->Dfi; b = 0 Actor 3: CB17 Dbo->Dfi
CB9 | bar: Actor 1 to b = 0 Actor 7
CB10 | bar: Actor 1 to b = 0 Actor 7
CB11 | bar: Actor 1 to b = 0 Actor 7
CB12 | bar: Actor 1 to b = 0 Actor 7
CB13 | bar: Actor 1 to b = 0 Actor 7
CB14 | Actor 1: CB6 Dfo->Dfi; f = 1 Actor 2: CB18 Dfo->Dfi; b = 0 Actor 3: CB7 Dbo->Dfi
CB15 | Actor 1: CB13 Dfo->Dfi; f = 1 Actor 2: CB18 Dbo->Dfi; b = 0 Actor 3: CB20 Dbo->Dfi
CB16 | Actor 1: CB17 Dfo->Dfi
CB17 | Actor 1: CB16 Dbo->Dbi; f = 1 Actor 2: CB5 Dfo->Dfi; b = 0 Actor 3: CB7 Dfo->Dfi; b = 0 Actor 4: CB8 Dbo->Dfi
CB18 | CB13 Dfo->Dfi | CB15 Dbo->Dfi | CB19 Dbo->Dfi | CB20 Dbo->Dfi | CB6 Dfo->Dbi | CB7 Dbo->Dbi | CB14 Dbo->Dbi
CB19 | Actor 1: CB13 Dfo->Dfi; f = 1 Actor 2: CB18 Dbo->Dfi; b = 0 Actor 3: CB20 Dbo->Dfi
CB20 | CB13 Dfo->Dfi | CB15 Dbo->Dfi | CB19 Dbo->Dfi | CB18 Dbo->Dfi | CB21 Dbo->Dbi
CB21 | Actor 1: CB20 Dfo->Dfi